Temporary Structure – meaning any structure that is so declared by owner and that is being used or  intended to be used for a specified purpose and for a specified limited period of time.

TEMPORARY STRUCTURE

Plan to be submitted to EMS Fire Safety prior to construction or erection of any temporary structure.

The following is required on plan.

- Plan to be to scale

- Site layout where structure is to be erected indicating surrounding structures and identifying safety distances.

- Size of structure to be erected.

- Purpose of structure (kitchen, hospitality, etc), should structure be subdivided, exits and travel distances to be addressed.

- Fire equipment and emergency signage layout to be addressed for temporary structure (marquees). EMS Fire Safety requires 1X9kg or 2 x 4,5kg fire extinguishers for every 100m2.

- Please note that no temporary structure or any structure may not obstruct any emergency exit or fire fighting equipment.

- Any fencing outside temporary structures to have exit gate in line with marquee emergency exits, as the term collapsible fencing does not apply.

- Type of surface on which temporary structure is to be erected on should be indicated on plan (grass, tar, concrete, paving) and how structure will be secured to deal with ‘wind load’.

- All electrical cabling to be used must be indicated and no cabling may be under the side sheeting of marquee on ground level, this must be underground or 0,5m distance away from side sheeting and not to pass in front of any emergency exit. It should be noted that the use of any heat emitting globes/lighting must not be directly secured to marquee material.

- Any open flame to be used in such temporary structures such as candles, Gas heaters, etc. This needs to be applied for in writing in terms of EMS by Laws.  And a permission letter for such use to be issued by EMS official

- Any draping proposed to be used must be indicated on plan, and once built a flame retardant certificate required.

- Floor coverings such as wood carpeting to be indicated and to be fire retardant. With certificate attached on site.

- Where raised floors are used for temporary structures, and such void below is used for service ducting, e.g. (electrical cabling) such void to be fitted with smoke detectors.

- Please note that amount of people required to be housed in such temporary structure needs to be indicated on plan. This will be determined in conjunction regarding the following, size of structure in square metres, amount and size of emergency exits, amount and type of furniture in such structure and type of use of structure.

- Any temporary structure to be used for evening use must be provided with emergency lighting.

- Generators being used have to be provided with last service history and electrical regulations to apply. These generators to be at least 3m away from such temporary structures and exhaust emission to be directed from structure. Generators that have built in fuel tanks are accepted, generators with separate tanks and drums for decanting to refuel, these need a separate applications with plans

- No vehicles to be parked directly against temporary structure.

Only once the plans have been submitted with all the above detail and have an approved stamp on the plan. Then only may the structure be erected.

Please note that the EMS tariff of charges apply for such approval of which       payment must be made in advance.

Payment of such structures made does not imply that approval of event had been given, should the need arise to change approved plans prior to event and new plans are submitted an additional payment will be required.

Please note that each plan will be assessed on its own merits and previous approvals may not be used as base for approval. These requirements are in line with National Building Regulations, Fire Safety By-Laws and good Fire Safety Practice.

Shaun Harrison					Andre Erasmus

Divisional Chief Events Management	Station Commander Events

Emergency Management Services		Emergency Management Services

City of Johannesburg				City of Johannesburg

Email shaunha@joburg.org.za		andreE@joburg.org.za

Tel 011 3810417				011 381 0430

Cell 0829660808				082 468 3834